Niman Power

West greater Noida, Sector -12, UP (201301)

JOB SAFETY ANALYSIS

| Project: |  | Date: |  |
| --- | --- | --- | --- |
| Job Title: | Replacement of switchboard | JSA no: |  |
| Location: |  | Page | 1 of |

JSA done by:

| Sr. | Name | Designation | Department | Remarks |
| --- | --- | --- | --- | --- |
| 1 |  |  | Consultant |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |
| 4 |  |  |  |  |
| 5 |  |  |  |  |

| Sl. No. | Activities | Hazards | Recommended Actions / Procedures & Control Measures |
| --- | --- | --- | --- |
| 1. | Obtain work permit & clearance | Working without permit is punitive | - Approval for work permit is to be availed - Approved copy of JSA to be displayed at site - Area barricading to be done. - Toolbox talks to be carried out for all personnel involved in activity. |
| 2. | wall dismantling if any | Fall hazard/ other equipment damage/Injury | - Ensure scaffolding is adequate for the bricks plus workers with a safety margin. - Safety PPE’s (Helmet, mask, goggles) shall be worn. - Safety belt/harness shall be worn while working at Height. - Extra hanging support shall be provided to pressurisation duct. - Message shall be given to F&S while dismantling the wall, there is chance of fire detector activation due to dust. |
| 3. | Cable trench erection | Fire hazard/ falling into trench | - safety goggles, Dust mask/respirator, gumboots shall wear during floor cutting and during Concrete pouring. - Work Area shall be barricade. - 30Ma ELCB shall be used in electrical machines for floor cutting. |
| 4 | Cable tray installation | Fire hazard/Injury | - Face shields shall be used during welding job. - 30ma ELCB shall be used in welding machine. - Work area shall be barricade. |
| 5. | Switchboard panel shifting/ installation | Falling load | - Use certified lifting equipment, trained operator/rigger, barricade unloading area. - Use pallet jack/forklift/rollers, team lifting, wear gloves. - 30ma ELCB shall be used in welding machine. - Work area shall be barricade. - Ensure the proper placement of panel on supports. - Chequer plate shall be installed at unused area on cable trench. |
| 6. | Cable joint | Fire hazard/Injury | - Isolation shall be taken for individual feeders for cable shifting and cable joint. - Only trained cable jointers are allowed to perform work. - Fire extinguisher must be available during heat work. - Maintain dry and clean work area. - Barricade testing area during HV testing. - Cable joints shall not be done in cable trench inside the substation switchgear room & shall be done outside of substation. |
| 7. | Dismantling of existing panels | Falling load | - Use certified lifting equipment, trained operator/rigger, barricade unloading area. - Use pallet jack/forklift/rollers, team lifting, wear gloves. - Chequer plate shall be installed at unused area on cable trench. |

| Sr. | Name | Designation | Department | Remarks |
| --- | --- | --- | --- | --- |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |
| 4 |  |  |  |  |
| 5 |  |  |  |  |

Reviewed and approved by

| HOD | Name | Designation | Sign |
| --- | --- | --- | --- |
| HOD user department |  |  |  |
| HOD of Concerned (Project Department) |  |  |  |
| HOD Operation Department |  |  |  |

Note:

To make JSA process effective, the defined job shall be broken down into sequential steps.  Actions / activities for each step shall be logical & linked with previous & forward action steps. All possible hazards associated with each job step shall be deliberated among team members and recorded carefully. JSA recommendations / control measures for each hazard / job step should be validated by team members & recorded in the Part-A of JSA sheet. Use additional JSA sheets as per requirements.

- Review of JSA shall be done by HOD of respective Operation Department and HOD of Concerned Maintenance Department. After review, respective HOD to put his signature with name & date.

- The Job shall be carried out with safety precautions as per JSA recommendations. HODs/ Fire & Safety & higher management personnel may also check compliance of JSA