“OISD hereby expressly disclaims any liability or responsibility for loss or damage resulting from the use of OISD Standards/Guidelines.”

OISD – STD – 244 Page No.39 STORAGE AND HANDLING OF PETROLEUM PRODUCTS AT DEPOTS AND TERMINALS INCLUDING STANDALONE CRUDE OIL STORAGE FACILITIES PROCESS FURNACE

G. Minimum Permissible Sizes of the Earthing Conductors:

| Size of the conductor shall be selected based the fault current that is required to be dissipated during emergencies. |  |  |  |
| --- | --- | --- | --- |
| Equipment |  |  | Size of the conductor |  |
| Main Earthing Grid |  |  | 50 mm x 6 mm GI strip |  |
| Lightening Arrester of the 2/4 Pole Structure |  |  | 40 mm x 6 mm GI strip |  |
| 2/4 Pole structure / Sub-Station equipments / VCB etc |  |  | 40 mm x 5 mm GI strip |  |
| Fence of the 2/4 pole structure / transformer yard |  |  | 25 mm x 3 mm GI strip |  |
| Power Transformer Neutral |  |  | 50 mm x 6 mm GI strip |  |
| Power Transformer Body |  |  | 40 mm x 6 mm GI strip |  |
| Fire Water Pump House |  |  | 25 mm x 6 mm GI strip |  |
| Building / Structure Columns |  |  | 40 mm x 5 mm GI Strip |  |
| Storage Tanks |  |  | 40 mm x 5 mm GI Strip |  |
| Push Button Stations |  |  | No. 8 SWG Solid GI Wire |  |
| Street Light Poles |  |  | 10 mm (3/8") GI Wire Rope |  |
| Small Equipment & Instruments |  |  | No. 8 SWG Solid GI Wire |  |
| Bonding of Pipes |  |  | 25 mm square copper strip / braided flexible cable. |  |
| Motors up to 3.7 Kw |  |  | No. 8 SWG Solid GI Wire |  |
| Motors above 3.7 Kw up to 30Kw |  |  | 10 mm (3/8") GI Wire Rope |  |
| Static Earth at Tanker / Wagon loading/ Unloading gantry |  |  | 40 mm x 6 mm GI strip. |  |
| Flexible cable for Static Earth |  |  | 10 Sq mm Copper flexible cable with lugs at one end and crocodile clip at other end. |  |

H. No of earth pits:

| This is minimum requirement and additional earth pits shall be made such as to maintain Grid Values below 1 Ohm. |  |
| --- | --- |
| Equipment | Nos |
| Earthing for LA | 2 Nos independent |
| For Di / Four Pole Structure, GO, Fence | 2 Nos (All metal bodies connected) |
| Neutral of the transformer | 2 Nos independent |
| Neutral of the D G Set | 2 Nos independent for each DG Set |
| Body of DG Set / control panel for DG Set | 2 Nos |
| Sub-station –PMCC Room | 4 Nos |
| Fire Pump House | 2 Nos |
| Air Comp House | 2 Nos |
| All structures Shed of Pump House / Fire Engine / Loading unloading Gantry / Air Compressor / Engg Store etc. | 2 Nos for each structures |
| Static Earth for Loading / unloading Gantry (Tank Truck) operations. | 2 Nos earth pits for 8 bay gantry. |
| Static Earth for Loading unloading Gantry (Tank Wagon) operations. | Min. 4 nos. earth pits for each (single/two spur) gantry. For rail track as per railway norms. |
| All 3 Phase Motors / FLP lights in each shed | 2 Nos |
| High Mast Tower (HMT) | 2 Nos for each HMT |
| Admin Blocks | 2 Nos |
| Data Processing | One for Metallic body parts of equipments and one for neutral of isolation-transformer |
| Inspection Platform / Watch Tower / Weigh Bridge | 1 Nos each |
| Water Storage Tanks (Fire Water Tank) | 2 per tank |
| Product Storage Tank | Minimum 2 nos and further as defined in Cl. B above. |